## Sheet1
Blue Ridge Technologies : Contractor Responsibility Guide
System Equipment | Division 25 |  |  |  | Division 26
| Furnish | Install | Wire | Note | Furnish | Install | Wire | Note
Centralized Panels (Switching or Dimming) | X |  |  |  |  | X | X | Tag / label device as required
Distributed Controllers (Switching or Dimming) | X |  |  |  |  | X | X | Tag / label device as required
Satellites (Switching or Dimming) | X |  |  |  |  | X | X | Tag / label device as required
Contactors | X |  |  |  |  | X | X | Tag / label device as required
Low Voltage Field Device - Wall Switch or Key Switch | X |  |  |  |  | X | X | Tag / label device as required
Low Voltage Field Device - Addressable Stations | X |  |  |  |  | X | X | Tag / label device as required
Low Voltage Field Device - 24VDC Occupancy Sensors | X |  |  |  |  | X | X | Tag / label device as required. Set timer to min. or zero. Set coverage pattern. Coordinate location with Div 25
Low Voltage Field Device - 24VDC Light Level Sensors (Indoor, Outdoor, or Daylight) | X |  |  |  |  | X | X | Tag / label device as required. Coordinate location with Div 25
Low Voltage Field Device - Faceplates |  |  |  |  | X | X |  | Engrave / label as required
System Warranty | X
System Installation Warranty |  |  |  |  | X
System Infrastructure | Division 25 |  |  |  | Division 26
| Furnish | Install | Wire | Note | Furnish | Install | Wire | Note
BACnet Network (Conduit and Raceway) |  |  |  |  | X | X |  | Pullstring
BACnet Network (Wire and Terminations) | X | X | X | Address Device
Line Voltage (Class I) Between Circuit Breaker and Lighting Controller and Lighting Load (Conduit, Raceway, Wire, and Terminations) |  |  |  |  | X | X | X | All 0-10V Signal wires shall be wired as Class I
Low Voltage (Class II) between Lighting Controller and Low Voltage Field Devices (Conduit, Raceway, Wire, and Terminations) |  |  |  | Address Stations and Satellites | X | X | X | All 0-10V Signal wires shall be wired as Class I
System Engineering | Division 25 |  |  |  | Division 26
| Furnish | Install | Wire | Note | Furnish | Install | Wire | Note
Submittal Package and As-built Drawings | X |  |  | Provide Div 26 with drawings | X |  |  | Provide Div 25 mark-ups for As-built
Sequence of Operations | X | X
Operators Interface | X | X
Programming and Configuration | X | X
System Checkout & Commissioning | X |  |  |  | X |  |  | Be present to address items
System Demonstration and Acceptance | X |  |  |  | X |  |  | Be present to address items
System Training | X
www.BRTint.com ¦ 800-241-9173 ¦ Blue Ridge Technologies® ¦ © 2014 Blue Ridge Technologies International, LLC. All Rights Reserved.